## 20-50-80KW
List of Parameters for Monitoring from Centralized System
Inverter Make |  |  | Growatt
Rating |  |  | 20 KW | 50 KW | 80 KW
Model Number |  |  | MID20KTL3-X | MAC50KTL3 LV | MAX 80KTL3 LV
Sl.No. | Modbus Register | Index No. in WebdynSun Gateway CSV file | Parameter Name | Parameter Description | Unit | Type | Value | Range | Remarks
Modbus Function Code : 3 - Read Holding Registers
1 | 00 | 1 | OnOff | Remote On/Off | - | UINT16 |  | - | On:1, Off:0
2 | 6 | 2 | Pmax H | Normal power | VA | UINT32 | (Hx65536+L)x 0.1 |  | H corresponds to Higher Order Byte (value of Index No.2) and L corresponds to Lower Order Byte (value of Index No.3).
3 | 7 | 3 | Pmax L
4 | 8 | 4 | Vnormal | Normal work PV voltage | V | UINT16 | x 0.1
5 | 9 | 5 | Fw version H | Firmware version (high) | - | ASCII |  | - | ASCII value to be read as much data as you see and then compare the value with standard ASCII value conversion tables to get the meaning.
6 | 10 | 6 | Fw version M | Firmware version (middle) | - | ASCII |  | -
7 | 11 | 7 | Fw version L | Firmware version (low) | - | ASCII |  | -
8 | 12 | 8 | Fw version 2H | Control Firmware version (high) | - | ASCII |  | -
9 | 13 | 9 | Fw version 2M | Control Firmware version (middle) | - | ASCII |  | -
10 | 14 | 10 | Fw version 2L | Control Firmware version (low) | - | ASCII |  | -
11 | 18 | 11 | Time start | Start time | s | UINT16
12 | 30 | 12 | Com | Modbus Device ID | - | UINT16 |  | 1-254 | 1-254
13 | 45 | 13 | Sys Year | System time- Year | - | UINT16 |  | -
14 | 46 | 14 | Sys Month | System time- Month | - | UINT16 |  | -
15 | 47 | 15 | Sys Day | System time- Day | - | UINT16 |  | -
16 | 48 | 16 | Sys Hour | System time- Hour | - | UINT16 |  | -
17 | 49 | 17 | Sys Min | System time- Min | - | UINT16 |  | -
18 | 50 | 18 | Sys Sec | System time- Second | - | UINT16 |  | -
19 | 88 | 19 | Modbus Version | Modbus Version | - | UINT16 | E.g.: 207 is V2.07 | -
Modbus Function Code : 04 - Read Input Registers
1 | 0 | 101 | Inverter Status | Inverter Running Status | - | UINT16 |  | - | 0:waiting, 1:normal, 3:fault
2 | 1 | 102 | Ppv H | Input power | W | UINT32 | (Hx65536+L)x 0.1
3 | 2 | 103 | Ppv L
4 | 3 | 104 | Vpv1 | PV1 voltage | V | UINT16 | x 0.1 |  | 0.1 is the multiplication factor to get the actual parameter value.
5 | 4 | 105 | PV1Curr | PV1 input current | A | UINT16 | x 0.1
6 | 5 | 106 | Ppv1 H | PV1 input power | W | UINT32 | (Hx65536+L)x 0.1
| 6 | 107 | Ppv1 L
7 | 7 | 108 | Vpv2 | PV2 voltage | V | UINT16 | x 0.1
8 | 8 | 109 | PV2Curr | PV2 input current | A | UINT16 | x 0.1
9 | 9 | 110 | Ppv2 H | PV2 input power | W | UINT32 | (Hx65536+L)x 0.1
| 10 | 111 | Ppv2 L
10 | 11 | 112 | Vpv3 | PV3 voltage | V | UINT16 | x 0.1
11 | 12 | 113 | PV3Curr | PV3 input current | A | UINT16 | x 0.1
12 | 13 | 114 | Ppv3 H | PV3 input power | W | UINT32 | (Hx65536+L)x 0.1
| 14 | 115 | Ppv3 L
13 | 35 | 116 | Pac H | Output Power | W | UINT32 | (Hx65536+L)x 0.1
| 36 | 117 | Pac L
14 | 53 | 118 | Eactoday H | Energy Generated -Today | kWH | UINT32 | (Hx65536+L)x 0.1 | 0-999
| 54 | 119 | Eac today L
15 | 55 | 120 | Eac total H | Energy Generated -Total | kWH | UINT32 | (Hx65536+L)x 0.1 | 0-99999
| 56 | 121 | Eac total L
16 | 57 | 122 | Time total H | Total Work Time | hh:mm | UINT32 | (Hx65536+L)x 0.1 | 0-9999
| 58 | 123 | Time total L
17 | 59 | 124 | Epv1_today H | PV1 Energy Generated -Today | kWH | UINT32 | (Hx65536+L)x 0.1 | 0-999
| 60 | 125 | Epv1_today L
18 | 61 | 126 | Epv1_total H | PV1 Energy Generated -Total | kWH | UINT32 | (Hx65536+L)x 0.1 | 0-99999
| 62 | 127 | Epv1_total L
19 | 63 | 128 | Epv2_today H | PV2 Energy Generated -Today | kWH | UINT32 | (Hx65536+L)x 0.1 | 0-999
| 64 | 129 | Epv2_today L
20 | 65 | 130 | Epv2_total H | PV2 Energy Generated -Total | kWH | UINT32 | (Hx65536+L)x 0.1 | 0-99999
| 66 | 131 | Epv2_total L
21 | 67 | 132 | Epv3_today H | PV3 Energy Generated -Today | kWH | UINT32 | (Hx65536+L)x 0.1 | 0-999
| 68 | 133 | Epv3_today L
22 | 69 | 134 | Epv3_total H | PV3 Energy Generated -Total | kWH | UINT32 | (Hx65536+L)x 0.1 | 0-99999
| 70 | 135 | Epv3_total L
23 | 91 | 136 | Epv_total H | PV Energy Total | kWH | UINT32 | (Hx65536+L)x 0.1 | 0-99999
| 92 | 137 | Epv_total L
24 | 93 | 138 | Temp1 | Inverter temperature | Deg.C. | UINT16 | x 0.1 | 0-100
25 | 94 | 139 | Temp2 | IGBT Temperature | Deg.C. | UINT16 | x 0.1 | 0-100
26 | 98 | 140 | P Bus Voltage | P Bus inside Voltage | V | UINT16 | x 0.1
27 | 99 | 141 | N Bus Voltage | N Bus inside Voltage | V | UINT16 | x 0.1
28 | 105 | 142 | Fault code | Inverter fault code | - | UINT16 |  | - | Refer Notes : &*1 table
29 | 106 | 143 | Fault Bitcode H | Inverter fault code | - | UINT32 |  | - | Refer Notes : &*8 table
| 107 | 144 | Fault Bitcode L
30 | 142 | 145 | V _String1 | PV String1 voltage | V | UINT16 | x 0.1
31 | 143 | 146 | Curr _String1 | PV String1 current | A | UINT16 | x 0.1
32 | 144 | 147 | V _String2 | PV String2 voltage | V | UINT16 | x 0.1
33 | 145 | 148 | Curr _String2 | PV String2 current | A | UINT16 | x 0.1
34 | 146 | 149 | V _String3 | PV String3 voltage | V | UINT16 | x 0.1
35 | 147 | 150 | Curr _String3 | PV String3 current | A | UINT16 | x 0.1
36 | 148 | 151 | V _String4 | PV String4 voltage | V | UINT16 | x 0.1
37 | 149 | 152 | Curr _String4 | PV String4 current | A | UINT16 | x 0.1
38 | 150 | 153 | V _String5 | PV String5 voltage | V | UINT16 | x 0.1
39 | 151 | 154 | Curr _String5 | PV String5 current | A | UINT16 | x 0.1
40 | 152 | 155 | V _String6 | PV String6 voltage | V | UINT16 | x 0.1
41 | 153 | 156 | Curr _String6 | PV String6 current | A | UINT16 | x 0.1
42 | 154 | 157 | V _String7 | PV String7 voltage | V | UINT16 | x 0.1
43 | 155 | 158 | Curr _String7 | PV String7 current | A | UINT16 | x 0.1
44 | 156 | 159 | V _String8 | PV String8 voltage | V | UINT16 | x 0.1
45 | 157 | 160 | Curr _String8 | PV String8 current | A | UINT16 | x 0.1
46 | 158 | 161 | V _String9 | PV String9 voltage | V | UINT16 | x 0.1
47 | 159 | 162 | Curr _String9 | PV String9 current | A | UINT16 | x 0.1
48 | 160 | 163 | V _String10 | PV String10 voltage | V | UINT16 | x 0.1
49 | 161 | 164 | Curr _String10 | PV String10 current | A | UINT16 | x 0.1
50 | 230 | 165 | Sac H | Output apparent power | W | UINT32 | (Hx65536+L)x 0.1
| 231 | 166 | Sac L
51 | 232 | 167 | ReActPowerH | Real Output Reactive Power | W | UINT32 | (Hx65536+L)x 0.1
| 233 | 168 | ReActPowerL
52 | 234 | 169 | ReAgtPowerMa×H | Nominal Output Reactive Power | VAR | UINT32 | (Hx65536+L)x 0.1
| 235 | 170 | ReAgtPowerMa×L
53 | 236 | 171 | ReActPower_Total H | Reactive power generation | kWH | UINT32 | (Hx65536+L)x 0.1
| 237 | 172 | ReActPower_Total L
Note :
1) | UINT32 is Unsigned 32 bit register : This will be read in two consecutive registers in Modbus. First Register will contain higher order bytes, second register will contain lower order bytes. In Centralized Monitoring System, Higher order and lower order bytes are to be combined to derive actual value of the parameter.
2) | UINT16 : Unsigned 16 bit integer
3) | All parameter values except the fault codes are in decimal integers. Fault code values are in Hexadecimal.
4) | &*1: Inverter fault code Bit:
| Fault type value | Meaning |  | Remarks
| 24 | "Auto Test Failed" |  | Fault type values are in hexadecimal. This can be either read as it is or if required to be converted into decimal values in Centralized Solar plant monitoring System.
| 25 | "No AC Connection"
| 26 | "PV Isolation Low"
| 27 | " Residual I High"
| 28 | " Output High DCI"
| 29 | " PV Voltage High"
| 30 | " AC V Outrange"
| 31 | " AC F Outrange "
| 32 | "Module Hot"
5) |  | &*8: Inverter fault code Bit:
|  | Value | Meaning | Remarks
|  | 0x00000002 | Communication error | Fault code bit values are in hexadecimal. This can be either read as it is or if required to be converted into decimal values in Centralized Solar plant monitoring System.
|  | 0x00000008 | Str Reverse or StrShort fault
|  | 0x00000010 | Model Init fault
|  | 0x00000020 | Grid Volt Sample diffirent
|  | 0x00000040 | ISO Sample diffirent
|  | 0x00000080 | GFCI Sample diffirent
|  | 0x00001000 | AFCI Fault
|  | 0x00004000 | AFCI Module fault
|  | 0x00020000 | Relay check fault
|  | 0x00200000 | Communication error
|  | 0x00400000 | Bus Voltage error
|  | 0x00800000 | AutoTest fail
|  | 0x01000000 | No Utility
|  | 0x02000000 | PV Isolation Low
|  | 0x04000000 | Residual I High
|  | 0x08000000 | Output High DCI
|  | 0x10000000 | PV Voltage high
|  | 0x20000000 | AC V Outrange
|  | 0x40000000 | AC F Outrange
|  | 0x80000000 | Temprature High

## 5&30KW
List of Parameters for Monitoring from Centralized System
Inverter Make |  |  | Growatt
Rating |  |  | 30 KW |  | 5 KW
Model Number |  |  | 30000TL3-S |  | 5000TL3-S
Sl.No. | Modbus Register | Index No. in WebdynSun Gateway CSV file | Parameter Name | Description | Unit | Type | Value | Range | Remarks
Holding Registers : FC3
1 | 00 | 1 | OnOff | The Inverter On/Off state and the auto start state | - | UINT16 |  | -
2 | 6 | 2 | Pmax H | Normal power | VA | UINT32 | (Hx65536+L)x 0.1 |  | H corresponds to Higher Order Byte (value of Index No.2) and L corresponds to Lower Order Byte (value of Index No.3).
| 7 | 3 | Pmax L
3 | 8 | 4 | Vnormal | Normal work PV voltage | V | UINT16 | x 0.1
4 | 9 | 5 | Fw version H | Firmware version (high) | - | ASCII |  | - | ASCII value to be read as much data as you see and then compare the value with standard ASCII value conversion tables to get the meaning.
5 | 10 | 6 | Fw version M | Firmware version (middle) | - | ASCII |  | -
6 | 11 | 7 | Fw version L | Firmware version (low) | - | ASCII |  | -
7 | 12 | 8 | Fw version 2H | Control Firmware version (high) | - | ASCII |  | -
8 | 13 | 9 | Fw version 2M | Control Firmware version (middle) | - | ASCII |  | -
9 | 14 | 10 | Fw version 2L | Control Firmware version (low) | - | ASCII |  | -
10 | 18 | 11 | Time start | Start time | s | UINT16
11 | 30 | 12 | Com | Modbus Device ID | - | UINT16 |  | 1-254
12 | 45 | 13 | Sys Year | System time- Year | - | UINT16 |  | -
13 | 46 | 14 | Sys Month | System time- Month | - | UINT16 |  | -
14 | 47 | 15 | Sys Day | System time- Day | - | UINT16 |  | -
15 | 48 | 16 | Sys Hour | System time- Hour | - | UINT16 |  | -
16 | 49 | 17 | Sys Min | System time- Min | - | UINT16 |  | -
17 | 50 | 18 | Sys Sec | System time- Second | - | UINT16 |  | -
18 | 73 | 19 | Modbus Version | Modbus Version | - | UINT16 | E.g.: 207 is V2.07 | -
Input Registers : FC4
1 | 0 | 101 | Inverter Status | Inverter Running Status | - | UINT16 |  | - | 0:waiting, 1:normal, 3:fault
2 | 1 | 102 | Ppv H | Input power | W | UINT32 | (Hx65536+L)x 0.1
| 2 | 103 | Ppv L
3 | 3 | 104 | Vpv1 | PV1 voltage | V | UINT16 | x 0.1 |  | 0.1 is the multiplication factor to get the actual parameter value.
4 | 4 | 105 | PV1Curr | PV1 input current | A | UINT16 | x 0.1
5 | 5 | 106 | PV1Watt H | PV1 input power | W | UINT32 | (Hx65536+L)x 0.1
| 6 | 107 | PV1Watt L
6 | 7 | 108 | Vpv2 | PV2 voltage | V | UINT16 | x 0.1
7 | 8 | 109 | PV2Curr | PV2 input current | A | UINT16 | x 0.1
8 | 9 | 110 | PV2Watt H | PV2 input power | W | UINT32 | (Hx65536+L)x 0.1
| 10 | 111 | PV2Watt L
9 | 11 | 112 | Pac H | Output Power | W | UINT32 | (Hx65536+L)x 0.1
| 12 | 113 | Pac L
10 | 26 | 114 | Energy today H | Energy Generated -Today | kWH | UINT32 | (Hx65536+L)x 0.1 | 0-999
| 27 | 115 | Energy today L
11 | 28 | 116 | Energy total H | Energy Generated -Total | kWH | UINT32 | (Hx65536+L)x 0.1 | 0-99999
| 29 | 117 | Energy total L
12 | 30 | 118 | Time total H | Total Work Time | hh:mm | UINT32 | (Hx65536+L)x 0.5 | -
| 31 | 119 | Time total L
13 | 32 | 120 | Temperature | Inverter temperature | Deg.C. | UINT16 | x 0.1 | 0-100
14 | 40 | 121 | Fault code | Inverter fault code | - | UINT16 |  | - | Refer Notes : &*1 table.
15 | 41 | 122 | IPM Temperature | IGBT Temperature | Deg.C. | UINT16 | x 0.1 | 0-100
16 | 42 | 123 | P Bus Voltage | P Bus inside Voltage | V | UINT16 | x 0.1
17 | 43 | 124 | N Bus Voltage | N Bus inside Voltage | V | UINT16 | x 0.1
18 | 48 | 125 | Epv1_today H | PV1 Energy today | W | UINT32 | Hx65536+Lx0.1 | 0-999 | Multiplication factor of 0.1 is applicable only for Low order byte.
| 49 | 126 | Epv1_today L
19 | 50 | 127 | Epv1_total H | PV1 Energy total | W | UINT32 | Hx65536+Lx0.1 | 0-99999
| 51 | 128 | Epv1_total L
20 | 52 | 129 | Epv2_today H | PV2 Energy today | W | UINT32 | Hx65536+Lx0.1 | 0-999
| 53 | 130 | Epv2_today L
21 | 54 | 131 | Epv2_total H | PV2 Energy total | W | UINT32 | Hx65536+Lx0.1 | 0-99999
| 55 | 132 | Epv2_total L
22 | 56 | 133 | Epv_total H | PV Energy total | W | UINT32 | Hx65536+Lx0.1 | 0-99999
| 57 | 134 | Epv_total L
23 | 58 | 135 | Rac H | AC Reactive power | Var | UINT32 | Hx65536+Lx0.1
| 59 | 136 | Rac L
24 | 60 | 137 | E_rac_today H | AC Reactive energy Today | Varh | UINT32 | Hx65536+Lx0.1 | 0-999
| 61 | 138 | E_rac_today L
25 | 62 | 139 | E_rac_total H | AC Reactive energy Total | kVarh | UINT32 | Hx65536+Lx0.1 | 0-99999
| 63 | 140 | E_rac_ total L
26 | 70 | 141 | V _String1 | PV String1 voltage | V | UINT16 | x 0.1
27 | 71 | 142 | Curr _String1 | PV String1 current | A | UINT16 | x 0.1
28 | 72 | 143 | V _String2 | PV String2 voltage | V | UINT16 | x 0.1
29 | 73 | 144 | Curr _String2 | PV String2 current | A | UINT16 | x 0.1
30 | 74 | 145 | V _String3 | PV String3 voltage | V | UINT16 | x 0.1
31 | 75 | 146 | Curr _String3 | PV String3 current | A | UINT16 | x 0.1
32 | 76 | 147 | V _String4 | PV String4 voltage | V | UINT16 | x 0.1
33 | 77 | 148 | Curr _String4 | PV String4 current | A | UINT16 | x 0.1
34 | 78 | 149 | V _String5 | PV String5 voltage | V | UINT16 | x 0.1
35 | 79 | 150 | Curr _String5 | PV String5 current | A | UINT16 | x 0.1
36 | 80 | 151 | V _String6 | PV String6voltage | V | UINT16 | x 0.1
37 | 81 | 152 | Curr _String6 | PV String6 current | A | UINT16 | x 0.1
38 | 120 | 153 | PV3 Voltage | PV3 input voltage | V | UINT16 | x 0.1
39 | 121 | 154 | PV3 Current | PV3 input current | A | UINT16 | x 0.1
40 | 122 | 155 | PV3Watt H | PV3 input power | W | UINT32 | Hx65536+L
| 123 | 156 | PV3Watt L
41 | 124 | 157 | Epv3_today H | PV3 Energy today | kWH | UINT32 | Hx65536+L | 0-999
| 125 | 158 | Epv3_today L
42 | 126 | 159 | Epv3_total H | PV3 Energy total | kWH | UINT32 | Hx65536+L | 0-99999
| 127 | 160 | Epv3_total L
43 | 128 | 161 | Faultcode H | Inverter fault code | - | UINT32 |  | - | Refer Notes : &*8 table
| 129 | 162 | Faultcode L
Note :
1) | UINT32 is Unsigned 32 bit register : This will be read in two consecutive registers in Modbus.First Register will contain higher order bytes, second register will contain lower order bytes. In Centralized Monitoring System, Higher order and lower order bytes are to be combined to derive actual value of the parameter.
2) | UINT16 : Unsigned 16 bit integer
3) | All parameter values except the fault codes are in decimal integers. Fault code values are in Hexadecimal.
4) | &*1: Inverter fault code Bit:
| Fault type value | Meaning |  | Remarks
| 24 | "Auto Test Failed" |  | Fault type values are in hexadecimal. This can be either read as it is or if required to be converted into decimal values in Centralized Solar plant monitoring System.
| 25 | "No AC Connection"
| 26 | "PV Isolation Low"
| 27 | " Residual I High"
| 28 | " Output High DCI"
| 29 | " PV Voltage High"
| 30 | " AC V Outrange"
| 31 | " AC F Outrange "
| 32 | "Module Hot"
5) |  | &*8: Inverter fault code Bit:
|  | Value | Meaning | Remarks
|  | 0x00000002 | Communication error | Fault code bit values are in hexadecimal. This can be either read as it is or if required to be converted into decimal values in Centralized Solar plant monitoring System.
|  | 0x00000008 | Str Reverse or StrShort fault
|  | 0x00000010 | Model Init fault
|  | 0x00000020 | Grid Volt Sample diffirent
|  | 0x00000040 | ISO Sample diffirent
|  | 0x00000080 | GFCI Sample diffirent
|  | 0x00001000 | AFCI Fault
|  | 0x00004000 | AFCI Module fault
|  | 0x00020000 | Relay check fault
|  | 0x00200000 | Communication error
|  | 0x00400000 | Bus Voltage error
|  | 0x00800000 | AutoTest fail
|  | 0x01000000 | No Utility
|  | 0x02000000 | PV Isolation Low
|  | 0x04000000 | Residual I High
|  | 0x08000000 | Output High DCI
|  | 0x10000000 | PV Voltage high
|  | 0x20000000 | AC V Outrange
|  | 0x40000000 | AC F Outrange
|  | 0x80000000 | Temprature High